{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":32,"n_cols":7,"rows_kept":32,"merged":[[0,0,0,6]],"flags":["formulas_cached_only"]}
["秀逸苏杭商务楼防雷工程数量统计"]
["序号","部位","配电箱名称","浪涌型号","单位","数量","备注"]
[1," ","AL-SY1、2","USF-BA35/3P；limp≥25KA（10/350μS ）； UP≤2.5KV","个",4,"商业照明配电总箱"]
[2,null,"A-2AL、B-2AL","USF-BA35/3P；limp≥25KA（10/350μS ）； UP≤2.5KV","个",2,"层照明配电总箱"]
[3,null,"C-1、2AL","USF-BA35/3P；limp≥25KA（10/350μS ）； UP≤2.5KV","个",2,"层照明配电总箱"]
[4,null,"AL-SY3、4","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",2,"商业照明配电总箱"]
[5,null,"ALS1~4"," ","个",24,"照明配电箱"]
[1," ","A、B3~25AL","USF-BA35/3P；limp≥25KA（10/350μS ）； UP≤2.5KV","个",46,"层照明配电总箱"]
[2,null,"C-3~5AL","USF-BA35/3P；limp≥25KA（10/350μS ）； UP≤2.5KV","个",3,"层照明配电总箱"]
[3,null,"ALB1~4"," ","个",84,"照明配电箱"]
[4,null,"AL-B1~3"," ","个",480,"照明配电箱"]
[5,null,"AT-XK","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",1,"消防控制室电源箱"]
[6,null,"AT-RD","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",1,"弱电机房电源箱"]
[1," ","A、B、C-APKSY1、2","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",6,"空调总配电箱"]
[2,null,"A、B-APK2~25","USF-BA35/3P；limp≥25KA（10/350μS ）； UP≤2.5KV","个",48,"空调总配电箱"]
[3,null,"C-1~5APK","USF-BA35/3P；limp≥25KA（10/350μS ）； UP≤2.5KV","个",5,"空调总配电箱"]
[4,null,"A、B-AP02；A、B-APE02","USF-BA35/3P；limp≥25KA（10/350μS ）； UP≤2.5KV","个",4,"走到照明总配电箱"]
[5,null,"A、B-2~25ALg","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",48,"走到照明箱"]
[6,null,"A、B-AD-AT1","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",2,"无机房电梯控制箱"]
[7,null,"A、B、C-AD-AT ","USF-BA35/3P；limp≥25KA（10/350μS ）； UP≤2.5KV","个",3,"普通电梯控制箱"]
[8," ","A、B、C-AP01；A、B、C-APE01","USF-BA35/3P；limp≥25KA（10/350μS ）； UP≤2.5KV","个",6,"消防总配电箱"]
[1," ","C-AT-PY1、2","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",2,"风机箱"]
[2,null,"A、B、C-AT-ZY1、2 ","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",6,"风机箱"]
[3,null,"C-1ALE","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",1,"商业应急"]
[4,null,"A、B-AT-XT","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",2,"消防电梯"]
[5,null,"B-AT-WYB","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",1,"屋面稳压泵"]
[null,null,"A、B-AC-FJ","USF-BA35/3P；limp≥25KA（10/350μS ）； UP≤2.5KV","个",2,"屋顶风机"]
[8," ","ALE-SY1、2","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",2,"应急照明 "]
[1," ","A、B-2~25ALE","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",48,"应急照明 "]
[2,null,"A、B-ALE-WD","USF-B80/4P；limp≥30KA（8/20μS ）； UP≤2.0KV","个",2,"屋顶应急照明 "]
[194,"总计",null,null,"个",837]
[{"$nulls":5}," "]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}